CITY OF WASHINGTON

INVITATION TO BID

FOR

DISTRIBUTION LINE UPGRADE

May 15, 2026

# INVITATION TO BID

The City of Washington is accepting sealed bids and qualifications for distribution line upgrade in the City of Washington.

Signed & sealed proposals will be received at the City Clerk’s Office, P.O. Box 296, 301 C Street, Washington, Kansas 66968, until 1:00 pm, June 1, 2026.  All bids should be clearly marked “Distribution Line Upgrade Bid”.

All submitted bids shall be honored for 60 days after the bid opening.

Bids will be opened at 1:00 pm, Monday, June 1, 2026, in the City Council Chambers.  Bids will be reviewed and a recommendation made to the City Council for consideration.

This project will have a completion deadline of December 1, 2026.

The City of Washington reserves the right to reject any or all bids with or without cause and to waive any irregularities.

If you have questions, please feel free to contact me at (785) 325-2284.

Sincerely,

Carl D. Chalfant, City Administrator

# GENERAL

A description of work to be performed is included.

The City of Washington reserves the right to reject any or all bids and to waive any informalities or irregularities therein.

The City Administrator may require that no bidder may withdraw a bid for a period of up to forty-five (45) days after the date and hour set for opening bids, but a bid may be withdrawn up to twenty-four (24) hours prior to expiration of the deadline for submitted bids.

Bids not submitted by the required deadline are ineligible for consideration and will not be opened.

# CONTACT INFORMATION

The point of contact for this project will be Carl D. Chalfant, City Administrator.

# TAXES

This project will be taxable.

# DESCRIPTION OF WORK

Electric distribution line upgrade.

Project #1: Beginning in the alley between W. 2nd St. and W. 3rd St. on D St. and running east approximately 480 feet in alley.

Description:

- Retire and Replace Pole A. Dead end, three pot pole, remove 3 transformers remove and reinstall (7) runs of triplex/quadplex, anchor/down guy, remove meter loop/reinstall meter loop. (3) new Transformers relocated to pole B.

- Retire and Replace Pole B. Install (3) new 50kva Transformers, cut-outs and arrestors, retire open 3 wire east/west, (3) runs triplex consumer, install new 4/0 quad to pole A to pick up services.

- Retire and Replace Pole C, remove and reinstall transformer, retire open 3 wire east/west, (2) cutout/arrestors, new #2 triplex west, (4) runs consumer triplex.

- Retire and Replace Pole D, retire open 3 wire east, new triplex east, (1) consumer triplex.

- Convert bottom of Pole E to double, Dead-end copper take off with 1/0 ACSR, possible OH Guy or sidewalk guy.

- Lay out old copper wire, pull in new 1/0 ACSR, and install #2 ACSR neutral approximately 480 feet, 3 phase.

- Retire open 3 wire, replace with new 1/0 triplex east one span, New #2 triplex one span west. From pole C to D.

End project #1.

Project #2: Location in utility easement running east and west between W. 4th St. and W. 5th St. form E St. to D St.

- Retire and Replace pole K, rehang new 37.5kva transformer, (3) runs triplex. Reinstall cutout and arrestors, install 1/0 triplex east to pole L.

- Retire and Replace pole L, (3) runs triplex, (1) reuse down guy, install 1/0 triplex to pole M to pick up 2 services. Backyard machine if possible.

- Retire and Replace pole M, remove transformer, (2) runs of triplex, (1) remove and reinstall do not hook up meter loop, new 1/0 ACSR from west to feed services, reattach telephone, backyard machine if possible.

- Leave existing pole N, (4) runs triplex, backyard machine if possible.

- Retire and Replace pole O, (3) runs triplex, backyard machine if possible.

- Retire and Replace pole P, (2) cutouts, (2) arrestors, and remove and reinstall transformer.

- String in new # 2 ACSR (9) spans, single phase, from pole H to pole Q, approximately 450 feet.

Project # 3: Location 910 D Street

- Retire and Replace Double circuit pole on east side of D in front of 910 D Street.

# MAP

See accompanying maps 1, 2, 3, and 4.

The yellow stars indicate the approximate location of each pole, which is marked with a letter identifier.